水汽分析取样装置

Water and Steam Integrated

Sampling Unit

操作使用说明书

Service Manual

吉林光大电力设备股份有限公司

Jilin Grand Power Equipment Co., Ltd

Index

目录

Part 1	Summary	4

概述	4

Part 2	CXD series sampling rack of chemical analysis	4

CXD系列化学分析取样架	4

1	Technical characteristics	4

技术特点	4

2	Working conditions	6

工作条件	6

3	Main technical indexes	6

主要技术指标	6

4	Outline dimension	7

外形尺寸	7

5	Debugging procedure	7

调试规程	7

Part 3	Reasons of common faults and elimination method	- 13 -

常见故障原因及排除方法	- 13 -

Part 4	Operating rules for CXD sampling rack of chemical analysis of water steam	- 16 -

CXD型水汽化学分析取样架操作规程	- 16 -

1	Preparations	- 16 -

准备	- 16 -

2	Cooling water	- 16 -

冷却水	- 16 -

3	Temperature inspector and electromagnetic valve	- 17 -

温度巡检和电磁阀	- 17 -

4	Running	- 17 -

运行	- 17 -

5	Meter	- 18 -

仪表	- 18 -

6	Security guarantee system	- 19 -

安全保证系统	- 19 -

7	Notice	- 19 -

注意事项	- 19 -

Part 5	Effect of the second drain valve which is newly added on the sampling rack in CXD series integrated device for sampling water steam	- 20 -

CXD系列水汽集中取样装置取样架新增二次排污阀的作用	- 20 -

Part 6	Additional comments for Operation rules of double drain valves of high temperature and pressure	- 22 -

双重高温高压排污阀操作规程的补充说明	- 22 -

1	Start drain	- 23 -

排污开始	- 23 -

2	Drain accomplished	- 23 -

排污结束	- 23 -

  - Summary

概述

This unit is adapted to pre-treatment the sample of water and steam for chemical analysis of thermo-equipment, manual sampling, on-line quality analysis of water and steam, computer supervising of the checked parameters.

本装置用于热力设备水汽化学分析样品的预处理、人工取样、水汽品质的在线分析、被测参数的计算机监督管理。

This unit composes of three basic sections: CXD series Sampling Unit of Chemical analysis, which functions in pre-treatment, manual sampling, providing eligible sample for on-line chemical analysis; Analysis instrument screen, on which installs on-line chemical analysis instrument and record displayer etc.; Computer control system, which functions in data collection, treatment, display, reports print, supervising, and communication with the computer in upper position etc.

本装置由三个基本部分组成：CXD系列化学分析取样架（通常所说的湿盘），完成样品的预处理、人工取样，为在线化学分析仪表提供合格的样品；分析仪表屏（通常所说的干盘），屏上安装在线化学分析仪表及记录显示器等；计算机管理系统，含数据采集、处理、显示、打印报表、监控、与上位机通讯等功能。

Users can select part of the unit or select all according to demand.

用户可以根据需要选定上述三部分中的部分或全部设备。

  - CXD series sampling rack of chemical analysis

CXD系列化学分析取样架

- Technical characteristics

技术特点

Taking a whole new route, the sampling rack acquires outstanding benefit that other racks cannot match, either domestic or overseas. In detail, the characteristics are as below:

取样架采用全新的技术路线，获得了现有国内外取样架无法比拟的效益。具体说来有如下特点：

  - The sampling rack adopts high-efficiency temperature-pressure reductor (patent) based on the fluid of high temperature and high pressure (such as water, steam etc.). When the fluid flows along the rack, the temperature and pressure will be reduced. So the rack has two functions of both the cooler of traditional sampling rack and the reductor.

取样架中采用了高温高压流体的高效降温降压器（专利产品），当高温高压流体（如水、汽等）流过该装置时，温度、压强同时降低，即具有传统取样架中冷却器和减压器二种功能。

  - The sampling rack is not equipped with pressure-only reductor, which avoids the traditional disadvantage of needing too much maintenance caused by reductor blockage.

取样架没有减压器，杜绝了取样架采用减压器易产生堵塞，需要精心维护的弊病。

  - The sample flows along the high-efficiency temperature-pressure reductor in a status of deep puffing, with high heat-exchange efficiency. Under the same conditions, the amount of cooling water is only 1/2 ~2/3 of the existing cooler.

样品流在高效降温降压器中的流动呈深度喘流状态，具有极高的热交换效率，在同样条件下冷却水的用量仅是现有冷却器1/2～2/3。

  - The sample flows along the pipes of the high-efficiency temperature-pressure reductor with speediness that helps the wall of pipes self-clean.

样品流在高效降温降压器的管道中流速很高，对管道壁有自清洗作用。

  - The sampling rack adopts a new-type filter, pole-style filter (patent), which can bar the mechanical impurity particles of both the steam media with diameter over 1.25mm and liquid medium with diameter over 1.05mm without changing the composition of the water sample basically. The pole-style filter is placed before the high-efficiency temperature-pressure reductor. And it has self-cleaning function because of large sample flow during the process of sample drain. After many operation tests in the special conditions and many years of running, the pole-style filter can avoid leakage and blockage, thus, it is maintenance-free product for life.

取样架中采用一种新颖过滤器——杆式过滤器（专利产品），仅截样品中介质为蒸汽1.25mm以上和介质为液态1.05mm直径的机械杂质颗粒，基本不改变水样的组成。杆式过滤器置于高效降温降压器前，在样品排污的过程中因样品流量较大，对杆式过滤器具有自清洗的作用。杆式过滤器经过多次特殊条件下的运行试验和现场多年的运行，不会产生泄漏和堵塞，所以本产品为终身免维护产品。

  - The sampling rack has a compact structure occupying small space, for example, ten-points sampling rack is 2.5m long, 0.65m wide, and 1.6m high, every point of sampling added, only 0.2m longer needed, without changing of width and height, therefore, the occupying area is only 3/5 of the current sampling rack.

该取样架结构紧凑，占地面积及空间小，例如，具有10个取样点的取样架长2.5m，宽0.65m，高1.6m，每增加一个取样点，只需加长0.2m，高、宽度不变，所以占地面积约为现有取样架的五分之三。

- Working conditions

工作条件

  - Ambient temperature: 5～40℃.

环境温度：5～40℃。

  - Power supply: 220V±10％，50Hz，2KVA

电源：220V±10％，50Hz，2KVA。

  - Cooling water

冷却水：

2.1.1   Temperature: <35℃.

温度：<35℃

2.1.2   The differential pressure between inlet and outlet of cooling water in the    temperature-pressure reductor: ＞ 0.15MPa

降温降压器冷却水进出口压差：＞ 0.15MPa，且不≤0.1 2MPa。

2.1.3   Flow: subjected to the number and the temperature of sampling points, and fifteen points of sampling are designed according to 31T/h.

流量：由取样点数及各点样品温度决定，15个取样点，按30 t/h设计

2.1.4   The cooling water of the temperature-pressure reductor adopts de-salted water, without rot, dirt or pollute.

冷却水对降温降压器无腐蚀、结垢、污染，一般采用除盐水。

- Main technical indexes

主要技术指标

  - Under the condition of the temperature lower than 620℃ and the pressure smaller than 34Mpa, the temperature of the treated water is about that of the cooling water plus 5℃(±1℃), the pressure is smaller than 0.3MPa.

水、汽样品温度<620℃，压力<34MPa条件下，处理后的水样温度约＝冷却水温度＋5℃（±1℃），压力<0.3MPa。

  - The flow of water sample: ≥1500ml/min.

水样流量≥1500ml/min。

  - The temperature patrol instrument of the outlet water sample is set at 40~50℃. The maximal absolute error of measurement should not be higher/lower than 1℃. Any exceeding of the alarm value will cause automatic alarming.  Under special condition, user can set the alarm value by himself.

出口水样温度巡检仪一般设定温度40～45℃，测量最大绝对误差不大于±1℃，超过限定报警。（特殊情况，用户可自行设定）

  - Pressure safety valve of the outlet water sample is set at 0.6~0.8MPa, adjustable.

出口水样压力安全阀设定值0.6～0.8MPa可调。

  - The inlet pressure of cooling water has limit alarm, which is set at 0.1~1.2MPa (or could be not set the upper limit alarm).

冷却水入口压力有越限报警，下限值设定在0.1MPa，上限值设定在1.2MPa或不设上限报警。

- Outline dimension

外形尺寸

Seventeen-points sampling rack is 1.9m long, 0.65m wide and 1.60m high.

17个取样点的取样架长4.0m，宽0.65m，高1.60m。

Note: According to user's need, it could be made into rack or combined type.

注：可根据用户需要，做成单元式或组合式。

- Debugging procedure

调试规程

  - Preparation before operation

运行前的准备

  - According to the system diagram, be familiar with the relative positions and functions among each parts of the sampling rack.

根据系统图，熟悉取样架各部件之间的相对位置和功能。

  - Adjust the pressure limits of pressure gauge or pressure switch on the contacts of cooling water, and check the alarm system whether normal

调整冷却水电接点压力表或压力开关上、下限的设定值，并检查报警系统是否正常。

  - Set the pressure limits of pressure gauge or pressure switch on the contacts of the inlet cooling water pipe at 0.1MPa~1.2MPa (or could not set the upper limit).

冷却水进口管的电接点压力表或压力开关的上限值可设定在1.2MPa或不进行上限设置，下限值设定在0.1MPa。

  - Do not set the pressure limits of pressure gauge on the contacts of the outlet cooling water pipe, which is not involved in control, only compared to that of the inlet cooling water pipe, to monitor the operating differential pressure of cooling water in the sampling rack.

冷却水出口管的电接点压力表不参与控制，不设上下限，只与入口电接点压力表对照，监控取样架冷却水工作压差。

  - Power on the temperature patrol instrument, set the sampling cycle and alarm values according to the instruction.

接通巡检仪电源，按说明书设定采样周期及各采样点的上、下限报警值。

  - The upper limit value of alarm is set at 40~45℃. Users can also set it themselves according to actual situation

上限报警值一般设定在40～45℃,用户也可根据实际情况设定。

  - The lower limit value of alarm is set at 0℃

下限报警值可设定在0℃。

  - Check the joints, seals, fasteners of the sampling rack whether loosed, check the valves whether closed.

检查取样架流路各种活节、密封件、紧固件都不准松动，阀门都处在关闭状态。

  - The commissioning of cooling water

冷却水投运

  - Open all in/out ball-valves of cooling water at all sampling points.

各样点、冷却水进、出口球阀都全开。

  - Open the valves for in/out cooling water pipes. The differential pressure between inlet and outlet of cooling water pipes should not be lower than 0.2Mpa, as normal.

开启冷却水进、出口管阀门。冷却水管路中进、出口压差应≥0.15MPa以上为正常。

  - Check the alarm

检查报警器是否正常

  - Adjust the upper limit value of pressure gauge or pressure switch on the contacts of the inlet cooling water pipe less than the actual pressure of the cooling water, if alarmed, regard the alarm as normal. Then set the upper limit value at 1.2MPa or more.

调整冷却水入口管电接点压力表或压力开关上限值<实际冷却水压力值，若报警，视为报警器使用正常。然后上限设定值为1.2MPa,或以上均可。

  - Adjust the lower limit value of pressure gauge or pressure switch on the contacts of the inlet cooling water pipe more than the actual pressure of the cooling water, if alarmed, regard the alarm as normal. Then recover the lower limit pressure 0.1MPa.

调整冷却水入口管电接点压力表或压力开关下限值>实际冷却水压力值，若报警，视为报警器使用正常。然后恢复下限设定值为0.1MPa。

  - After finish the alarm debugging, adjust the differential pressure between inlet and outlet of cooling water at a stable status of more than 0.12MPa.

报警调试结束后，调整冷却水进、出口压差稳定在＞0.12Mpa的状态下方可。

  - The commissioning of high-temperature and high-pressure system

高温高压系统投运

Only when the cooling water system works in normal condition, the high-temperature and high-pressure system can be operated.

只有冷却水运行正常状态下，才能进行高温高压系统的运行。

  - Open the manual sampling valve and the flowmeter knob fully.

手工取样阀、流量计旋扭全开。

  - Close first inlet and second inlet valves of sampling water, drain valve and flow control valve.

水样一次进口阀、水样二次进口阀、排污阀、流量控制阀全关闭。

  - Open the first inlet valve of the sampling rack slowly; watch the connections of filter, the second inlet valve and drain valve to check whether leaking, if it leaks, fasten it with special spanner. (Note to work with gloves, in order to prevent scalding).

慢慢开启取样架水样一次进口阀，观察过滤器，水样二次进口阀，排污阀联接部位是否有渗漏，若有渗漏，用专用板手紧固（注意要带手套，防止烫伤）。

  - If the connections of the first inlet valve of sampling water, drain valve and filter are confirmed no leakage, open the drain valve slowly and fully. After the temperature of water rises to stable, close the drain valve quickly. When discharge the sewage again, open and close the drain valve quickly. And the time of drain is about ten seconds.

水样一次进口阀、排污阀、过滤器的联接部位无渗漏后，再缓慢开启排污阀，达到全开。待排污样水温上升平稳后，迅速关闭，再次排污时排污阀要快开快关，排污的时间约为10秒左右。

  - Open the second inlet valve of sampling water slowly; watch the system of high-temperature and high pressure whether leaking. If it leaks, close the first inlet valve, repair the leakage, then open the second inlet valve again.

再缓慢打开水样二次进口阀，观察高温高压系统是否有渗漏，若有渗漏，关闭一次阀将渗透处处理好，再打开二次进口阀。

  - Open flow control valve slowly, watch the floater of the flowmeter rising, if the water sample flows smoothly, that will be considered normal.

慢慢开启流量控制阀，观察流量计，浮子上升，水样流淌顺利为正常。

  - Adjust the flow-limiting valve; make the flowmeter displaying a flow about 500ml/min. (Control the flow of manual sampling to satisfy the meter flow-rate need). Open the injection valve to let the instrument start working.

调节限流阀，使流量计的流量为500ml/min左右即可。（控制手工取样流量，满足仪表流量需要）。开启进样阀，仪表投入运行。

  - Overheating protection test for electromagnetic valve

电磁阀超温保护试验

  - Turn down the inlet flow of the cooling water (reduce the opening of the valve), watch the display of the temperature patrol instrument, when exceeds the upper limit temperature①, alarms, after reaches the upper limit temperature②, the electromagnetic valve starts working to cut off the flow of the sample water, which certifies the normality of overheating protection. Then turn up the inlet flux of cooling water (increase the opening of the valve), recover the normal working status.

将冷却水进口管流量逐渐调小（阀门开度减小），观察温度巡检仪上显示温度达到上限①报警温度时，报警器报警，达到上限②的报警温度时电磁阀动作，切断水样流路，此时证明超温保护工作正常，然后将冷却水进口管流量调大（阀门开度增大），恢复正常运行状态。

  - Close the first valve; open the drain valve; release the flow pressure of the sample water between the sampling rack and the manual sampling plate; the electromagnetic valve starts working to open the cutting waterway, and then close the drain valve, open the first valve, recover the normal working status.

关闭一次阀，打开排污阀，将取样架与手工取样盘之间内的样水样流路中的压力泄掉，则电磁阀动作，切断水路被打开，再关闭排污阀，打开一次阀恢复正常运行状态。

Note:  the upper limit temperature① is the alarm temperature; the upper limit temperature② is the action temperature of electromagnetic valve.

注：上限①为报警温度,上限②为电磁阀动作温度。

  - The alarm of cooling water pressure reducing

冷却水水压降低报警

During the operation, when the inlet pressure of cooling water lower than 0.1MPa, alarms, at the same time, the electromagnetic valve closes all actions, cuts off the water circuit. If these happened, found the reasons and repair it (reasons, see the descriptions in the malfunction analysis column), then the cooling water recovers the normal working status. If the electromagnetic valve does not action—not opened, do according to 5.4.2.

在运行过程中，当冷却水入口压力≤0.1MPa时，报警器报警，同时电磁阀动作――闭合，切断水样流路，此现象发生后，找出原因处理好后（原因在故障分析栏内叙述）冷却水恢复正常运行状态。若电磁阀不动作——打开。按5.4.2操作进行处理。

  - Debugging of the safe valve

安全阀的调试

The safe valve is set behind the outlet of the flow-control valve and before the flowmeter. The working pressure is set at 0.6MPa and acting pressure is set at 0.8MPa. When the flow circuit has overloading pressure, the safe valve automatically unloads. The safe valve is regulated well when leaving the factory. Normally does not need regulating during the rack working. When it operates for a period of time or finds any malfunction, need be rechecked and regulated. The method as below:

安全阀安装在流量控制阀出口后压力表之前，设定其工作压力0.6MPa，动作压力0.8MPa，当流路水压超压后安全阀自动卸荷，安全阀在设备出厂前已调好，一般在设备运行时不用调试。当运行一段时间检修或发现安全阀失灵，需重新检查调试安全阀时其方法如下：

Remove the safety valve, at the rear of the safe valve, connect pressure meters between the connective pipes of the safe valve (range of 1MPa), close the water circuit to the instrument, regulate the manual sampling valve to raise the interior pressure of the sample water pipe to 0.6~0.8MPa. The safe valve starts to work, and will be closed when the pressure lowers to 0.5~0.6MPa, then recover the normal working status. Otherwise, regulate the setting value of the safe valve until reach the status above mentioned. Unload the pressure meter and install the safe valve.

拆下安全阀，在安全阀后安全阀接管间接上压力表（量程1MPa），关闭通往仪表的水样通路，调节手工取样阀，使水样管内压力上升。直到0.6～0.8MPa。安全阀动作开通，压力降至0.7～0.6MPa时，安全阀关闭，管路恢复正常运行状态。否则需调安全阀设定值，直到达到上述状态为止。卸掉压力表、装好安全阀。

  - Stop running operation

停止运行操作

First, close the first inlet valve of the sample water, then close the second inlet valve of the sample water and the drain valve, when the sample water stops flowing, close the inlet and outlet valve of cooling water, then close the power supply of the temperature detector.

首先关闭水样一次进口阀，依次关闭二次水样进口阀、排污阀，待水样断流后，关闭冷却水管入出口阀门，再关闭温度巡检仪电源。

  - Maintenance

维护

  - Open the drain valve periodically, the drain method referring to 5.3.4 in page 7 and operation of drain referring to 4.3.2 in page 20. The drain cycle is subject to the purity of the sample water and the operational experience.

定期开启排污阀，排污方法参照P7页5.3.4和P19页4.3.2运行排污。排污周期，视水样的纯度，由运行经验而定。

  - The Self-cleaning function of pole-style filter. During the rack working, the flow of high-pressure sampling water washes the pole-style filter at random in the drain process of sampling water, which is a self-cleaning process.

杆式过滤器的自清洗作用。在设备运行时，样水在排污的过程中，高压样水流体对杆式过滤器有一个高压乱流冲刷的过程，这个过程就是一个自清洗的过程。

  - Reasons of common faults and elimination method

常见故障原因及排除方法

| Serial Number序号 | Fault Classification故障分类 | Phenomenon现 象 | 可 能 原 因 Possible reasons | Treatment suggestions 处 理 建 议 |
| --- | --- | --- | --- | --- |
| Ⅰ | The system of cooling water冷 却 水 系 统 | 1. The inlet pressure of cooling water is not enough 1.冷却水入口压力不足 | 1. The outlet pressure of the pump is lower 1.泵出口压偏低 | 1. Raise the outlet pressure of the pump 提高泵出口压力 |
|  |  | 2. The differential pressure between inlet and outlet of cooling water is not sufficient 2.冷却水入、出口压差不够 | 1. The pressure of original inlet is lower 1.原入口压偏低 2. The resistance of outlet pipe is larger or the outlet pipe is block 2.出口管路阻力偏大或堵塞 | 1. Raise the outlet pressure of the pump 1.提高泵入口压力 2. Dredge the pipes, open the outlet valve larger 2.疏通出口管路，开大出口阀门 |
|  |  | 3.The flow of cooling water is not sufficient 3.冷却水流量不够 | 1. The outlet diameter of pump is smaller 1.泵出口直径小 2. The diameter of pipes are smaller 2.管路直径不够 3. Pipes or pump has leakage 3.管路或泵有泄漏 | 1. Enlarge the diameter of the pump outlet 1.加大泵出口 2. Enlarge the diameter of pipes 2.加大管路直径 3. Check the pump and pipes, not allow leakage 3.检查泵和管路不允许有泄漏 |
| Ⅱ | The system of cooling water水 样 系 统 | 1. The temperature of sample water is higher 1.水样温度偏高 | 1.The temperature of cooling water is higher 1.冷却水温度偏高 2. The cooling water is not sufficient 2.冷却水量不足 2.1 Cooling water pipes is block 2.1冷却水管路堵塞 2.2 Pump or pipes of cooling water has leakage 2.2冷却水泵或管路泄漏 2.3 The differential pressure between inlet and outlet of cooling water is lower 2.3冷却入出口压差偏低 2.4 The opening of inlet and outlet valves of cooling water is inadequate 2.4冷却水入出口阀门开度不够 2.5 The filter net blocked is block 2.5过滤网堵塞 | 1. Decrease the temperature of cooling water 1.降低冷却水温度 2.1 Dredge the cooling water pipes 2.1疏通冷却水管路 2.2 Check the pump and pipes, not allow leakage 2.2检查水泵及管路不 准管泄漏 2.3 Increase the outlet water drainage 2.3加大出口排放量 2.4 Enlarge the opening of cooling water valves 2.4加大冷却水阀门开度 2.5 Clean the filter net 2.5清洗过滤网 |

| Ⅱ | The system of water sample 水 样 系 统 | 2.The flow of water is not sufficient or there is no sample water flow 2.水样流量不够或无水样流量 | 1. The first and second high-pressure valves are not fully opened 1.一、二次高压阀未全开 2. The opening of flowmeter, flow-control valve, flow-limit valve is inadequate 2.流量计、流量控制阀、限流阀开度不够 - Temperature and pressure reductor blocked 降温降压器堵塞 - Incoming pressure of sample water is not enough 样水来压压力不够 | 1.Open the opening of the first and second high-pressure valves larger 1.开大一、二次高压阀 2.Enlarge the opening of the flowmeter reasonably, control the opening of flow -limit valve 2.合理加大流量，控制限流阀的开度 - Find out the reason and dredge the pipes 查明原因疏通管路 |
| --- | --- | --- | --- | --- |
|  |  | 3. sample water is turbid 3.水样浑浊 | 1. Pipeline is not clean 1.管路不清洁 2. Drain is not completely 2.排污不彻底 3. Medium is turbid in boiler 3.锅炉内介质浑浊 | 1. Clean pipeline 1.清洁管路 2. Drain periodically 2.定期排污 3. Run Continuous blowdown system and Improve the water quality of boiler 3.开连排系统或改善炉内水质 |
| Ⅲ | 管 路 系 统 The system of pipeline | Inlet and outlet of cooling water and joints have leakage冷却水出入口及连接部位渗漏，电磁阀系统渗漏低压管接口渗漏 | 1. Fastening screw loosed 1.紧固螺丝松动 2. Gasket not well-positioned or damaged 2.密封垫未垫好或损坏 | 1. Fasten the screw 1.紧固好螺丝 2. re-seal or change the gasket 2.重新密封或更换密封垫 |
| Ⅳ | The protection system of overheating and over pressure 超温 超压 保护 系统 | 1. No alarm output 1.无报警输出 | 1.the setting of parameter is error 1.参数设置不对 2. The temperature patrol instrument break down 2.巡检仪故障 3. Heat resistance damaged 3.热电阻损坏 4. Disconnection 4.断线 | 1. Reset 1.重新设置 2. Repair the temperature patrol instrument 2.修理巡检仪 3.Change 3.更换 4. Change the wires 4.换线 |

| 四 | The protection system of overheating and over pressure 超 温 超 压 保 护 系 统 | 2. Alarms but electromagnetic not actions 2.有报警输出电磁阀不动作 | 1.Wrong connection 1.线接反 2. Winding burned out 2.线圈烧断 3. Diode damaged 3.二极管损坏 4.Action pole in the valve blocked 4.阀内活动杆卡死 | 1. Reverse the connection 1.两根线换线 2. Change the winding 2.更换线圈 3. Change the diode 3.更换二极管 4. Open and repair 4.拆开修理 |
| --- | --- | --- | --- | --- |
|  |  | 3. Electromagnetic can’t open automatically after closed 3.电磁阀动作关闭后，不能自动打开 | 1. Pressure of the flow circuit is higher 1.流路压力大 2. Temperature of pipeline not reduced 2.管路温度未下降 3. Spring blocked 3.弹簧卡死 | 1. Close the first valve, open the drain valve, unload and reduce pressure 1.关闭一次阀，打开排污阀、泄荷减压 2. Wait some time until the temperature dropped 2.等候一段时间待温度下降 3. Repair the spring and let it move freely 3.修复弹簧让其动作自如 |
|  |  | 4. Electromagnetic can’t fully close after motion 4.电磁阀动作后关不严 | 1. Flow circuit is not clean, attached foreign matter 1.流路不清洁有异物贴附 2. Action pole blocked in the valve 2.阀内活动杆卡住 3. Gasket damaged 3.密封垫损坏 | 1.Clean the flow circuit and the closing contact surface of the valve 1.清洁管路及阀闭合接触面 2. Uninstall and repair 2.拆下修理 3. Change the gasket 3.更换密封垫 |
|  |  | 5. Safe valve does not act 5. 安全阀不动作 | 1. Slider in the valve blocked 1.阀内滑块卡住 2. Safe valve port blocked 2.安全阀口堵塞 3. Pressure regulation of safe valve is higher 3.安全阀调压过大 | 1. Uninstall and repair 1.拆下修复 2. Clean the pipeline and inlet 2.清洗管路及入口 3. Lower the pressure of spring (ordinarily not occurred)3.下调弹簧压力（一般不会发生） |
| 四 | The protection system of overheating and over pressure 超 温 超 压 保 护 系 统 | 6. Safe valve unclosed 6.安全阀不闭合 | 1. Valve seat is not clean 1.阀座不干净 2.Spring damaged 2.弹簧损坏失灵 3. Valve needle surface damaged 3.阀针面破坏 | 1.Clean the valve seat 1.清洗阀座 2.Change the spring 2.更换弹簧 3. Change the valve needle surface 3.更换阀针 |
|  |  | 7. Safe valve not closed tightly 7.安全阀关不严 | 1. Valve seat is not clean 1.阀座不干净 2.Spring damaged 2.弹簧损坏失灵 3. Valve needle surface damaged 3.阀针面破坏 | 1.Clean the valve seat 1.清洗阀座 2.Change the spring 2.更换弹簧 3. Change the valve needle surface 3.更换阀针 |

  - Operating rules for CXD sampling rack of chemical analysis of water steam

CXD型水汽化学分析取样架操作规程

- Preparations

准备

Check if the prime high pressure valves on every sampling point, second point, drain valve and manual flow control valve are all closed and the high pressure joints and screws on cooling water pipeline are screwed up. If not, screw them up.

在设备末投入运行前应检查取样架各点上的一次高压阀，二次高压阀，高压排污阀和盘面上的手工流量控制阀是否全部关闭及取样架上的高压接头（降温降压器的一级和二级连接的样水管路接头）和冷却水管路的螺丝是否松动，并拧紧。

- Cooling water

冷却水

Before running the device, cooling water should be circulated first until the requirement of the water has been met. Then the device can be started. Requirements of the cooling water are list below:

在设备投入运行前，要先进行冷却水的运行，达到本产品对冷却水的要求后，方可进行设备的运行工作。本产品对冷却水的要求如下：

  - Temperature of cooling water 1inlet should be less than 35℃

冷却水的入口温度应<35℃；

  - Ensure pressure difference of cooling water will be ≥0.15 MPa, and must not be ≤0.12MPa,inlet pressure minus out pressure(of the cooling water ) equals working pressure difference.(can be gotten from inlet/outlet pressure gauge of the rack surface.)

冷却水的工作压差应保证≥0.15 MPa，且不得≤0.12 MPa，冷却水的压差是冷却水入口压力—冷却水出口压力=工作压差。（从盘面的出、入口压力表可得知）

  - Cooling water flow must be reached (commented in the technical protocol).

要满足设备所需的冷却水流量。（技术协议有说明）。

  - If the rack experiences a power failure in running process, cooling water should be kept flowing in case of operator casualty and derive accidents.

设备正常工作后，在取样架工作电源失电条件时冷却水不可断流，以防止发生运行人员和设备事故。

- Temperature inspector and electromagnetic valve

温度巡检和电磁阀

Power is supplied, the temperature inspector and electromagnetic valve would then work from each according to its ability: display the temperatures, give under pressure alarm, overheating alarm, electromagnetic valve working prompt of each points.

将电源接通，温度巡检和电磁阀就各尽其能；显示各点温度、欠压报警、超温报警、电磁阀工作等各项功能。

- Running

运行

After confirm the above points the device is ready to be started as following steps:

在前几项确认完成后，就可以让设备投入运行了。步骤如下；

  - Open the manual sampling valve and rotameter together to avoid pressure increment of the low pressure pipeline and leakage and rotameter damage in case of operation faults. The above two valves can be kept open and needn’t be closed even if the boiler is stopped.

将手工取样盘面上的手工取样阀、浮子流量计全部打开，以防止误操作后造成，低压管路压力增大，泄漏和流量计的损坏。以上二个阀门可以常开，即使停炉也不需要关闭。

  - High pressure vales of the rack (prime, second and drainage valves) must follow the “open/close all” principle to avoid high temperature and pressure fluid damaging the valve needle, ensuing normal operation of the device. The point is of great importance and keeps it in mind.

取样架上的高压阀（一次阀、二次阀、排污阀）在开启和关闭过程中，要全开全闭，以防止高温高压流体对阀针的冲刷和损坏，保证设备的正常运行，这一点非常重要，切记。

  - Open a high pressure prime valve slowly until it is opened thoroughly, then open the drain valve (all should be opened) to clear the drainage.

设备投入时应慢慢开启某一点上的一次高压阀，直至全部打开，再开启排污阀（全部打开），进行管道的排污工作，具体排污时间可按；

  - Start the boiler to drain: drain away the water in the pipe, then close drain valve quickly until the pipeline has reached the high temperature.

启炉排污：将管道内的冷水全部排出，待管道达到高温后，然后快速关闭排污阀。

  - Draining in process: open the drain valve fully and quickly, after 5～10 minutes, close it quickly. If sampling water is dirty, repeat the above process 1～3 times in normal.

运行排污；将排污阀快速全部开启5——10秒钟后再快速关闭，如样水较脏可多次进行上述工作，正常下1——3次就可以了。

After drain, open the second high-pressure valve, make the sampling water flow through the filter into temperature-pressure reductor, and watch high pressure fitting and pipeline if leak. After normal, open the second high-pressure valve fully. The operation of High-pressure is completed.

当排污工作结束后，慢慢开启二次高压阀让样水通过过滤器流入降温降压器中，并观察高压接头和管路是否有泄漏现象。正常后将二次阀全部打开既可。高压部分操作完毕。

Note: The flow control valve in the surface of the manual sampling plate is also a high-pressure valve. (In the front of valve is the high-pressure part, behind the valve is into the low-pressure pipeline). Forbid taking the high-pressure valve (the first or second valve) in the sample rack to adjust the flow of sampling water. Otherwise the high-pressure valve will be in half-close state, and damaged, can not work normally.

注意：手工取样盘面上的流量控制阀也是高压阀（阀前是高压部分，阀后进入低压管路）。禁止用取样架上的高压阀（一次或二次阀）进行调节样水流量，否则会使高压阀处于半关闭状态下，造成高压阀损坏，不能正常工作。

- Meter

仪表

Certain amount of water is needed before using the meter. First open each meter valve that holds the path of sample water to the meter, If sample water flow is more  or less than  the desired flow, valve for limiting flow on the pipeline where the manual sampling valve is can be adjust ed. The flow limiting valve is turned in the direction that decreases the opening to increase sample water flow or in the opposite to get a less flow.

投入仪表需一定量的水样。首先打开各路样水通往仪表的仪表阀，当样水流量在仪表处大或小时，可调节在手工取样阀上的管路中安置的仪表限流阀，限流阀门往开度小的方向调节，仪表样水增大，反之为小。

- Security guarantee system

安全保证系统

  - Overheating alarm: Overheating alarm is set in the temperature inspector. When the sample water reaches the upper limit temperature, the temperature patrol instrument will alarm automatically. When the sample water reaches the upper limit temperature②, the instrument commands the electromagnetic valve close at the same time, cut off sample water to ensure the security.

超温报警：温度巡检中设有超温报警，当样水温度达到上限报警值时，温度巡检会自动蜂鸣报警，当样水温度达到上限②报警值时，温度巡检自动报警的同时指令电磁阀关闭，切断样水，确保安全。

  - Under pressure alarm: When the cooling water is in zero flow due to unexpected factors or under pressure, the pressure gauge at contacts will make under pressure alarm, and at the same time commands the electromagnetic valve close, cut off sample water to ensure the security.

欠压报警：当冷却水因意外因素产生断流或欠压时，电接点压力表（入口）或压力开关产生欠压报警，同时也指示电磁阀关闭，切断样水，确保安全。

  - Low-pressure safety valve: For some reasons (do not open the flow-limit valve after close the sample water of the meter used) that make the pressure of pipes increase, or exceeds the security valve of 0.8MPa, the low-pressure safety valve automatically opened drains, until the pressure recovered to 0.7～06Mpa, closed automatically.

6.3     低压安全阀：当某种因素（仪表使用的样水关闭后未把仪表限流阀打开）使管道压力增大。当超过安全值时（≥0.8MPa）低压安全阀将自动打开，排泄，待压力恢复到0.7Mpa-0.6Mpa时安全阀自动关闭。

- Notice

注意事项

7.1      Lead the cooling water into at first, the pressure and differential pressure should satisfy the use requirement (Instruction).

冷却水要首先投入，压力、压差要保证使用要求（说明书）

7.2     Manual sampling valve and the flow meter should be opened firstly or be opened usually, to prevent the damage caused by misoperation.

手工取样阀，流量计要先开或常开，防止误操作造成不应有的损坏。

7.3    The electromagnetic valve is controlled by the indication of temperature inspector & pressure gauge of contacts or pressure switch, and is closed when acting, at that time there is no water sample at the sampling point, and it is self-locked. If restarted, working staff should close the first high-pressure valve on sampling rack, and then open the drain valve and release the pressure of device that lowers the temperature and the pressure; the electromagnetic valve is able to open in non-working status, the drain valve can be closed consequently. After the cause has been found and eliminated, and cooling water is circulating normally, the water can be led into the first high-pressure valve. Sampling rack or electromagnetic valve can be started then.

电磁阀受温度巡检和电接点压力表或压力开关的指示控制，动作时是关闭状态，取样点无水样，并于自锁状态，如重新开启工作人员应关闭取样架上的一次高压阀，再打开排污阀，将降温降压器内的压力泄掉后，电磁阀才能自动打开（不工作）再关闭排污阀，待找出原因并消除动作原因后，冷却水正常运行后再投入一次高压阀，使设备取样架或电磁阀投入工作。

  - Effect of the second drain valve which is newly added on the sampling rack in CXD series integrated device for sampling water steam

CXD系列水汽集中取样装置取样架新增二次排污阀的作用

Our corporation is a professional pioneer producer of sampling rack in China, Based on guiding principle of “Focus on customer’s need; ensure monitoring device quality of power equipment and customer’s satisfaction“, the second drain valve which is newly added on the sampling rack in CXD series integrated device for sampling water steam is placed at the high temperature and pressure point. Thus the safe operation of the sampling rack device can be guaranteed.

我公司是国内较早生产取样架的专业公司，本着“关注顾客 确保电力设备运行监测装置质量 确保顾客满意”的质量方针，对我公司的产品：CXD系列水汽集中取样装置—取样架部分高温高压样点上上新增二次排污阀门，以保证取样架设备的安全运行。

Our market service men have recently investigate many power plant and conclude that sampling rack produced by different producer, whether native or imported valve is applied, after having been running for certain time, inner leak will be  unavoidable at the high temperature and pressure point and result in constant-contaminated phenomenon of the sampling rack. Therefore our corporation specially organized the related personnel and the valve producer staff to analyze the problem in detail. The conclusion is:

近来我公司市场服务人员在多家电厂了解到：各家公司生产的取样架，无论是以进口阀门还是国产阀门作为排污阀门的产品，在运行一段时间后，高温高压样点上或多或少均会出现内漏的问题，而导致取样架常排污的现象发生。因此，我公司专门组织相关人员对此种现象进行了细致的分析，并请阀门厂家人员共同研究，认为主要是由于：

When drains at water (steam) sample point, though the particle of impurity has come through prime valve, second valve and filter, still all particles are concentrated at the drain valve inlet before draining operation. When sampling rack is in draining operation, drain valve must stand the overall wash of the high speed moving particles, the overwhelming energy of motion will bring a sever test to the flow path in the valve, since it is very probable that there is abrasion of the flow path surface that could make the valve sealing failed, which will result in inner leak of the drain valve.

水（汽）样点进行排污时，由于水（汽）样品带来的细小杂质微粒虽然已经通过样点一次阀、样点二次阀及过滤器，但所有杂质微粒在排污操作前全部集中在排污阀门的入口处，当取样架进行排污操作时，排污阀要经受高速运动中的杂质微粒的全面冲刷，而这些杂质微粒由于具备了强大的动能，这对于阀中的流路部分是个严峻的考验，因此在运行的过程中极易冲琢流路面，而造成阀门密封不严，导致了排污阀门内漏现象。

When staffs at the production field haven’t followed the “open/close all” operating rule hasn’t been followed. The possibility is greater of situation described in 1 occurring. Considering the above two points, based on the creed of being responsible for our customer, design of double drain valves at the high temperature and pressure point of the sampling rack is adopted to provide addition security.

现场人员未严格按照取样架操作规程进行排污阀的“全开、全关”操作，这样更易加剧1中所述情况的发生。综上两点，我公司本着对用户负责的态度，提出在取样架高温高压样点采用双重排污阀的方式，起到双保险的作用，见图中所示（排污二次阀）。

This diminishes the occurrence of constant-contaminated phenomenon of the sampling rack led by the inner leak effectively, and in the same time release the staff from maintenance greatly. After all, this is very favorable for the device running in security.

这样可有效的减少由于排污阀门内漏而造成的取样架常排污现象的发生，同时也可大大的降低现场操作人员对排污阀门的维护，这对于整台取样架设备的安全运行是十分有利的！

  - Additional comments for Operation rules of double drain valves of high temperature and pressure

双重高温高压排污阀操作规程的补充说明

In running process, inner leak is mostly brought up by incorrect operations. That is to say, the “open/close all” principle hasn’t been followed in operation.

在设备运行过程中，排污阀发生内漏的原因多为操作不规范而造成，即未能按照运行规程的“全开、全关”方式进行操作。

For security of drain valve of high pressure, even if it is in leaking situation described above, bring in a second drain valve of high pressure in the bottom of prime valve(refer to the above figure).

为保证高压排污阀因操作不当引起内漏后，仍能保证设备的安全运行，在高温高压样点的排污阀下端，增设一只高压排污二次阀（见上图）。

Operation rules:

操作规程：

- Start drain

排污开始

  - Open the prime drain valves of high pressure one and all.

将高压排污一次阀全部打开。

  - Open slowly the second drain valve until requirement of drain has been met. The feasible time of the running device should be 5－10 seconds. It is better to implement drain of the first time when the new sample water is coming. Drain can be executed repeatedly if required.

在缓慢开启高压排污二次阀，达到排污要求。设备在正常运行时的排污时间为5－10／秒，初次排污时间为新样水到来为好。根据要求可反复多次排污。

- Drain accomplished

排污结束

  - Second drain valve of high pressure should be closed up first

首先关闭高压排污二次阀，关严。

  - Prime drain valve of high pressure should be closed up after that.

再关闭高压排污一次阀，关严。

Note: Double drain valves of high pressure should be opened/closed one and all, it is forbidden to use it as flow regulating valve, be sure to keep it in mind!!!

注：双重高压排污阀在工作时一次排污阀操作时要全开、全关，决不可以做排污流量调节阀使用，切记！！！

结盟天下    广交朋友

吉林光大电力设备股份有限公司

资料如有改动，本公司保留修改权

地址：吉林高新技术产业开发区2号路57号

P.C.：132013

Tel：86 432 66098886     Fax：86 432 66098888

Jilin Grand Power Equipment Co., Ltd

.

The manufacturer reserves the right to vary the content described in this manual

Address: 57 the 2nd Street, High-tech industrial development district of Jilin City

Post code: 132013

Tel: 86 432 66098886

Fax: 86 432 66098888